Note to users: items shown in red indicated edits / selections that need to be made to tailor the specification for the application.

Metraseal Modular Pipe Seal

- General:

  - Provide modular link type pipe wall penetration seals as indicated on the contract drawings or as needed.

  - Modular pipe seal shall consist of interlocking links of elastomer selected for the application.

  - Modular pipe seal shall be suitable for installation into core drilled openings or into a wall sleeve.

  - Modular link seal shall be rated for 20 PSI.

- Products:

  - Modular link type pipe wall seal shall be:

    - MetraSeal® Model E as manufactured by the Metraflex Co. Chicago, IL.  Model E features EPDM links with zinc dichromate plated carbon steel hardware (used for general applications for temperatures from -40 to +250⁰ F.)

    - MetraSeal® Model ES as manufactured by the Metraflex Co. Chicago, IL.  Model ES features EPDM links with Stainless steel hardware (used for applications in a corrosive environment, for temperatures from -40 to +250⁰ F.)

    - MetraSeal® Model P as manufactured by the Metraflex Co. Chicago, IL.  Model P features Nitril links with zinc dichromate plated carbon steel hardware (used for applications with exposure to hydrocarbons for temperatures from -40 to +210⁰ F.)

    - MetraSeal® Model PS as manufactured by the Metraflex Co. Chicago, IL.  Model P features Nitril links with stainless steel hardware (used for applications in a corrosive environment and exposure to hydrocarbons for temperatures from -40 to +210⁰ F.)

    - MetraSeal® Model HT as manufactured by the Metraflex Co. Chicago, IL.  Model HT features Silicone links with zinc dichromate plated carbon steel hardware and plates (used for high temperature applications from -40 to +400⁰ F.)

  - Options

    - Modular link seal shall be provided with a galvanized steel wall sleeve that is cast in place in a concrete wall.  Wall sleeve shall have a 2” wide water stop welded on both sides.  Galvanized steel wall sleeve shall be WSCSG by the Metraflex Co. Chicago, IL.

    - Modular link seal shall be provided with a Sch 40 PVC wall sleeve that is cast in place in a concrete wall.  Wall sleeve shall have a 2” wide water stop welded on both sides.  PVC wall sleeve shall be WSPVC by the Metraflex Co. Chicago, IL.

- Execution.

  - Rubber modular link type pipe wall penetration seals joints shall be installed per manufacturer’s instructions.

  - Use manufacturers documentation to properly select the correct size and number of links.

# Text boxes

Product Specifications