Medium Pressure Rubber Flex Connector

Product Specifications

- Provide medium pressure rubber connectors as indicated on the contract drawings or as needed to compensate for thermal expansion or to eliminate the transmission of vibration and noise through the piping system.

- Products:

  - Medium pressure rubber connector shall be Style 201® as manufactured by the Metraflex Co. Chicago, IL.

  - Materials.

    - Medium pressure rubber flex connector shall be of corrugated Neoprene with internal nylon fabric reinforcement.

    - Each corrugation crest shall have an internal stainless steel reinforcement.  Each corrugation bottom shall have an external stainless steel ring reinforcement.

    - Medium pressure rubber flex connector clamps on to plain end pipe with stainless steel bands with zinc plated carbon steel T-Bolt clamps.

  - Maximum operating conditions shall be 75 PSI at 210⁰ F.

- Execution.

  - Rubber joints shall be installed per manufacturer’s instructions and in accordance to Rubber joints FSA's "Technical Handbook: Non-Metallic Expansion Joints and Flexible Pipe Connectors."

  - Refer to catalog data for rubber flex connector movement capabilities.