Flexible Hose Connectors.

Product Specifications

- General

- Provide flexible hose connector(s) as indicated on the contract drawings or as required to accommodate any thermal expansion, contraction or seismic movement of the piping system.

- Flexible hose connectors shall be capable of compensating for lateral movement and vibration.

- Flexible hose connectors shall be manufactured complete with section of corrugated metal house, compatible braid, with inlet and outlet connections as required.

- For flammable liquid or gas service up to 4”, flexible hose connector shall be CSA / AGA certified.

- Products

- Flexible hose connectors to be manufactured by The Metraflex Company®, Chicago, IL.

- Corrugated Hose

B.1 Stainless Steel

B.1.1 	Type 304

B.1.2	Type 321

B.1.3	Type 316

    - Bronze

- Braid

  - 304 Stainless Steel braid shall be used for any series 300 stainless steel hose.

  - Bronze braid shall be used for any bronze hose.

D	Fittings Materials of construction and end fitting type shall be consistent with pipe material and equipment/ pipe connection fittings.  Copper fittings shall not be attached to stainless steel hose.

E	Flexible hose connector(s) shall be rated with an operating pressure in accordance with the table below.  The operating pressure shall be based on burst pressure with a 4 to 1 safety factor.

2.1	Pressure rating

- Flexible Hose Connector with Stainless Steel Hose

Working			Working

Pressure at 70° F.	Pressure at 70° F.

Size	Single Braid		Double Braid

½”	1100  PSI		1525  PSI

¾”	792			1267

1”	571			914

1 ¼”	531			850

1 ½”	472			755

2”	500			750

2 ½”	387			600

3”	288			431

4”	232			371

5”	200			245

6”	170			300

8”	212			260

10”	175			220

12”	160			220

Flexible Hose Connector with Bronze Hose

Working			Working

Pressure at 70° F.	Pressure at 70° F.

Size	Single Braid		Double Braid

½”	566  PSI		753  PSI

¾”	468			622

1”	334			444

1 ¼”	306			407

1 ½”	297			395

2”	210			279

2 ½”	194			258

3”	166			221

4”	109			175

- Execution

- Install flexible hose connectors where indicated on contract documents.

B. Install and guide per manufacturers’ installation instructions and Mechanical Contractors Association of America “Guidelines for Quality Piping Installations”.