Flexible Hose Connectors.

Product Specifications

- General

- Provide flexible hose expansion loop(s) as indicated on the contract drawings or as required to accommodate any thermal expansion, contraction or seismic movement of the piping system.

- Flexible hose expansion loops shall be manufactured complete with two parallel sections of corrugated metal house, compatible braid, 180 deg return bend, with inlet and outlet connections.  Field fabricated loops shall not be acceptable.

- Flexible loops shall be capable of movement in the ±X, ±Y, and ±Z planes.

- Flexible hose expansion loops shall impart no thrust loads to system support, anchors or building structure.

- For flammable liquid or gas service up to 4”, flexible expansion loops shall be CSA / AGA certified.

- All flexible hose expansion loops shall be manufactured in accordance with the documented manufacturers weld procedure specifications.  The procedure qualification record shall be used to document the execution of this procedure and shall follow the general “guidelines” of ASME Section IX.  Each individual welder shall conform to the in-house procedure qualification record and be qualified prior to each production lot.  The testing of each individual welder shall be documented in a welding procedure qualification record.

- Products

- Flexible hose expansion loops to be "Metraloop®” as manufactured by The Metraflex Company®, Chicago, IL.

- Corrugated Hose

B.1 Stainless Steel

B.1.1 	Type 304

B.1.2	Type 321

B.1.3	Type 316

    - Bronze

C	Braid

C.1	304 Stainless Steel braid shall be used for any series 300 stainless steel hose.

C.2	Bronze braid shall be used for any bronze hose.

D	Fittings Materials of construction and end fitting type shall be consistent with pipe material and equipment/ pipe connection fittings.  Copper fittings shall not be attached to stainless steel hose.

E	Flexible hose expansion loops shall have a factory supplied, hanger / support lug located at the bottom of the 180deg return.

F	Flexible hose expansion loop(s) shall be furnished with a plugged FPT to be used for a drain or air release vent.

Loop Size		FPT Size

1” – 6”			3/8”

8” and Larger	½”

G	Flexible hose expansion loop(s) shall be rated with an operating pressure in accordance with the table below.  The operating pressure shall be based on burst pressure with a 4 to 1 safety factor.

Flexible Expansion Loop with Stainless Steel Hose

Working			Working

Pressure at 70° F.	Pressure at 70° F.

Size	Single Braid		Double Braid

½”	1100  PSI		1525  PSI

¾”	792			1267

1”	571			914

1 ¼”	531			850

1 ½”	472			755

2”	500			750

2 ½”	387			600

3”	288			431

4”	232			371

5”	200			245

6”	170			300

8”	212			260

10”	175			220

12”	160			220

Flexible Expansion Loop with Bronze Hose

Working`		Working

Pressure at 70° F.	Pressure at 70° F.

Size	Single Braid		Double Braid

½”	566  PSI		753  PSI

¾”	468			622

1”	334			444

1 ¼”	306			407

1 ½”	297			395

2”	210			279

2 ½”	194			258

3”	166			221

4”	109			175

- Execution

- Install and guide per manufacturers’ installation instructions and Mechanical Contractors Association of America “Guidelines for Quality Piping Installations”.

- Flexible hose expansion loop return fitting shall be supported to allow movement.

- For steam applications, the operating pressure shall be based on burst pressure with an 8 to 1 safety factor.