Automatic Air Release Valve:

Product Specifications

- General:

- Automatic Air Release Valves shall be float operated and designed to release accumulated air from high points in a piping system while the system is in operation and under pressure.

- Air Release Valves suitable for water service

- Products

- Manufacturer: Air release valve shall be joints shall be “MetraVent” as manufactured by The Metraflex Company®, Chicago, IL.

- The valve body and cover shall be constructed of ASTM A126 Class B cast iron for working pressures up to 300 psig at 150 deg F.

- The orifice and linkage shall be constructed of SAE 30303 Stainless Steel.  The float shall be ASTM A0240 Stainless Steel.

- The orifice seal button shall be flouroelastomer.

- The cover shall be bolted to the valve body and sealed with a flat gasket. Resilient seats shall be replaceable and provide drop tight shut off to the full valve pressure rating.

- Valves shall have FNPT threaded inlets and outlets. The body inlet connection shall be hexagonal for a wrench connection.

- The valve shall have an additional NPT connection for the addition of gauges, testing, startup filling and system draining.

3.	Execution

A.	Automatic Air Release Valve shall be installed at system high points and where indicated by system designer.

B.	When installed in finished areas and when specified, valve discharge can be piped to drain