Sample Specifications for Strainers

Model TS - Threaded Cast Iron Y-Type Pipeline Strainer:

Strainers to be of the “Y” pattern type. Strainer body to be ASTM A126-B cast iron with threaded end connections and 304 stainless steel screen. Screen access by way of threaded or bolted cover and blowoff plug. Operating pressures and temperatures to be 250psi-steam@400°F and 400psi-wog@150°F. For water service, 1/4” thru 2" sizes to have 20 mesh screens, 2-1/2" & 3" to have .045 perforations*. Y-type pipeline strainers to be model “TS”** as manufactured by The Metraflex Company®, Chicago,IL.

* Other materials, perforations, mesh linings are available

** For domestic manufacture specify model “SM”

Model TF - Flanged Cast Iron Y-Type Pipeline Strainer:

Strainers to be of the “Y” pattern type. Strainer body to be ASTM A126-B cast iron with flanged end connections and 304 stainless steel screen. Flange drilling to be class 125 or 250 as appropriate for the application. Screen access by way of bolted cover and blowoff plug. Operating pressures and temperatures to be 125psi - steam @ 350°F / 175psi-wog @ 150°F (Model TF) or 250psi-steam @ 400°F / 400psi-wog @ 150°F (Model TF2). For water service, 2" thru 3" sizes to have .045 perforations, 4" thru 16" to have .125 perforations*. Y-type pipeline strainers to be model “TF”** as manufactured by The Metraflex Company®, Chicago, IL

* Other materials, perforations, mesh linings are available

** For domestic manufacture specify model “M-1-M”

Model BS - Threaded Bronze Y-Type Pipeline Strainer:

Strainers to be of the “Y” pattern type. Strainer body to be ASTM B-62 bronze with threaded end connections and 304 stainless steel screen. Screen access by way of  threaded cover and blowoff plug. Operating pressures and temperatures to be 150psi-steam@450°F and 300psi-wog@100°F. For water service, 1/4” thru 2" sizes to have 20 mesh screens, 2-1/2" & 3" to have .062 perforations*. Y-type pipeline strainers to be model “BS” as manufactured by The Metraflex Company®, Chicago, IL

* Other materials, perforations, mesh linings are available

Model BSJC - Sweat End Bronze Y-Type Pipeline Strainer:

Strainers to be of the “Y” pattern type. Strainer body to be ASTM B-62 bronze with sweat end connections and 304 stainless steel screen. Screen access by way of threaded cover and blowoff plug. Maximum operating pressure and temperature to be 300psi-wog@100°F. For water service, 1/4” thru 2" sizes to have 20 mesh screens*. Y-type pipeline strainers to be model “BSJC” as manufactured by The Metraflex Company®, Chicago, IL

* Other materials, perforations, mesh linings are available

Model B-1 - Basket Type Pipeline Strainer:

Strainers to be of the removable basket type. Bodies to be ASTM A126-B cast iron with bolted or clamp style cover and bottom drain (8" thru 16" provided with side drain). Pressure class and flange drilling to be class 125 (B-1) or 250 (B-2) as appropriate for the application. Strainer basket to be of T304 stainless steel material with perforated sides and solid bottom*.  For water service, 2" thru 3" sizes to have .045 perforations, 4" thru 16" to have .125 perforations*. Basket to be provided with an integral handle for removal and size of perforations to be appropriate for the media. Basket strainers to be model “B-1" as manufactured by The Metraflex Company®, Chicago, IL

* Other materials, perforations, mesh linings are available

Model SA - Pump Suction Diffuser:

Provide pump suction diffusers on the inlet side of pumps. Body to be ASTM A126-B cast iron with bolted cover, pressure gauge tapping, and bottom drain. Flange drilling to be class 125 with a rated working pressure of 175psi, maximum operating temperature of 300°F. Provide with equal size flanges or reduced outlet flange as required. Strainer screen to be of .125 perforated T304 stainless steel material with a removable 20 mesh start up screen. Suction diffusers to be provided with internal straightening vanes to minimize turbulence. Suction diffusers to be model “SA" as manufactured by The Metraflex Company®, Chicago, IL

Series F900 - Foot Valve:

Foot valves shall be flanged, center-guided, silent, non-slam type. Valves shall have cast iron body, bronze disc/seat, Buna-N seal, stainless steel spring, and stainless steel basket. Flange drilling to be ANSI class 125. Valve inlet stainless steel screening, shall be basket shaped equal to full flow area of the valve. Buna-N seal shall be so designed to provide an initial contact of bronze to buna-N with final contact being metal to metal to prevent destruction of buna-N seal ring. Foot valves shall be “Model #F900" as manufactured by The Metraflex Company®, Chicago, IL.

Model BW/BL - Butterfly Valve:

Butterfly valves shall be of the wafer (BW) or lug (BL) body style. Cast iron body with ductile iron nickel coated, bronze, or 316 stainless steel disc. Pressure rating of 200 psi @ 250°F (EPDM seat) and 200°F (Buna-N seat). Valves to be supplied with 10-position lever lock handle, gear operator, or bare stem for actuation. Butterfly valves shall be “Model BW/BL" as manufactured by The Metraflex Company®, Chicago, IL.

# Text boxes

Product Specifications