Sample Specifications for Valves

Product Specifications

Series 700 - Wafer Style Silent Check Valve:

Check valves shall be of the wafer style, center-guided, silent, non-slam type. Check valves to have cast iron body, bronze disc and seat, and stainless steel spring*. Sizes 2" thru 6" to be ANSI B16.1 class 125/250. Sizes 8" and 10" to be either ANSI B16.1class 125 or 250 as appropriate for the application. Valve to have a cracking pressure of ¼ to ½ psi, and fully open at a flow velocity of 4 fps. Operation of the valve shall not be affected by position of installation. Valve shall be capable of fully closing prior to reversal of flow, and shall eliminate water hammer. When specified, a Buna-N seal shall be furnished to provide bubble tight shutoff. All component parts shall be field replaceable. Check valves shall be “Factory Mutual” approved through 12" size. Silent check valves shall be “CV700" series as manufactured by The Metraflex Company®, Chicago, IL.

* Optional materials available

Series 900 - Globe Style Silent Check Valve:

Check valves shall be of the flanged globe style, center-guided, silent, non-slam type. Check valves to have cast iron body, bronze disc and seat, and stainless steel spring*. Flange drilling to be ANSI B16.1 class 125 or 250 as appropriate for the application. Valve to have a cracking pressure of ¼ to ½ psi, and fully open at a flow velocity of 4 fps. Operation of the valve shall not be affected by position of installation. Valve shall be capable of fully closing prior to reversal of flow, and shall eliminate water hammer. When specified, a Buna-N seal shall be furnished to provide bubble tight shutoff. All component parts shall be field replaceable. Check valves shall be “Factory Mutual” approved through 12" size. Silent check valves shall be “CV900" series as manufactured by The Metraflex Company®, Chicago, IL.

* Optional materials available

Series “Chexx” - Dual Disc Check Valve:

Check valves shall be of the wafer style, non-slam, dual disc type with torsion spring. Check valves shall have cast iron body, bronze or aluminum bronze disc and seat, and stainless steel spring. The body shall be one piece construction incorporating a Buna-N seal. Opening and closing of the valve must utilize a lift and pivot action to prevent seal wear. The stop and pivot pins shall be resiliently mounted to prevent wear and vibration during operation. Valves shall be “Factory Mutual” approved through 12" size. Dual disc check valves shall be “CHEXX" series as manufactured by The Metraflex Company®, Chicago, IL.

* Optional materials available

Series F900 - Foot Valve:

Foot valves shall be flanged, center-guided, silent, non-slam type. Valves shall have cast iron body, bronze disc/seat, Buna-N seal, stainless steel spring, and stainless steel basket. Flange drilling to be ANSI class 125. Valve inlet stainless steel screening, shall be basket shaped equal to full flow area of the valve. Buna-N seal shall be so designed to provide an initial contact of bronze to buna-N with final contact being metal to metal to prevent destruction of buna-N seal ring. Foot valves shall be “Model #F900" as manufactured by The Metraflex Company®, Chicago, IL.

Model BW/BL - Butterfly Valve:

Butterfly valves shall be of the wafer (BW) or lug (BL) body style. Cast iron body with ductile iron nickel coated, bronze, or 316 stainless steel disc. Pressure rating of 200 psi @ 250°F (EPDM seat) and 200°F (Buna-N seat). Valves to be supplied with 10-position lever lock handle, gear operator, or bare stem for actuation. Butterfly valves shall be “Model BW/BL" as manufactured by The Metraflex Company®, Chicago, IL.