Note to users: items shown in red indicated edits / selections that need to be made to tailor the specification for the application.

Spherical Rubber Flex Connector with Kevlar Reinforcement

Product Specifications

- Provide spherical rubber connectors as indicated on the contract drawings or as needed to compensate for thermal expansion or to eliminate the transmission of vibration and noise through the piping system.

- Products:

  - Single spherical rubber connector shall be Mightysphere® as manufactured by the Metraflex Co. Chicago, IL.

  - Double spherical rubber connector shall be Double Mightysphere® as manufactured by the Metraflex co., Chicago, IL.

  - Rubber connector shall be of the molded spherical type. Rubber expansion joint shall be peroxide cured EPDM rubber.

  - Rubber reinforcement shall be Kevlar tire cord.

  - Flange anchor ring shall be solid carbon steel embedded into the bead seal.

  - Flanges shall be split galvanized plate carbon steel plate floating flanges with 150 lb. drilling.

  - Options.

    - Control units must be furnished in unanchored applications, or as recommended by the manufacturer.

    - Pump intake shall be equipped with a CRV Flange insert

    - Pump discharge shall be equipped with Vane Flange insert straightening Vane.

- Execution.

  - Rubber joints shall be installed per manufacturer’s instructions and in accordance to Rubber joints FSA's "Technical Handbook: Non-Metallic Expansion Joints and Flexible Pipe Connectors."

  - When used as expansion joints, spherical rubber joints shall be anchored and guided in accordance with EJMA recommendations.

  - Refer to catalog data for rubber expansion joints movement capabilities.